## Equipment list
Tag | Tag status | Description | DEXPI class | Area | Lifecycle | Data from the specification | Nozzles | Source | Topology id
BACAN1 | source | LPF tank BACAN1 | Tank | ar.lpf | modified | heating medium change: live steam → hot-water loop (90 °C) | 5 | p.2 §3. Consommateurs process et modifications | eq.lpf_tank_an1
BACS04 | source | LPF tank BACS04 | Tank | ar.lpf | modified | heating medium change: live steam → hot-water loop (90 °C) | 5 | p.2 §3. Consommateurs process et modifications | eq.lpf_tank_s04
BACS05 | source | LPF tank BACS05 | Tank | ar.lpf | modified | heating medium change: live steam → hot-water loop (90 °C) | 5 | p.2 §3. Consommateurs process et modifications | eq.lpf_tank_s05
ECH-030 | source | Emergency plate exchanger 1/3 | PlateHeatExchanger | ar.well | new | capacity fraction: 50 %; design heat flow rate: 8747 kW | 4 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.emerg_hx_a
ECH-031 | source | Emergency plate exchanger 2/3 | PlateHeatExchanger | ar.well | new | capacity fraction: 50 %; design heat flow rate: 8747 kW | 4 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.emerg_hx_b
ECH-032 | source | Emergency plate exchanger 3/3 | PlateHeatExchanger | ar.well | new | capacity fraction: 50 %; design heat flow rate: 8747 kW | 4 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.emerg_hx_c
GEA | source | LPF steam user GEA | CustomEquipment | ar.lpf | modified | steam supply pressure: 4 bar eff. | 1 | p.2 §3. Consommateurs process et modifications | eq.lpf_gea
K3 | source | LPF steam user K3 | CustomEquipment | ar.lpf | modified | steam supply pressure: 4 bar eff. | 1 | p.2 §3. Consommateurs process et modifications | eq.lpf_k3
MESSO | source | LPF steam user MESSO | CustomEquipment | ar.lpf | modified | steam supply pressure: 4 bar eff. | 1 | p.2 §3. Consommateurs process et modifications | eq.lpf_messo
P-030 | source | Well-water pump 1/3 | CentrifugalPump | ar.well | new | capacity fraction: 50 %; design volume flow rate: 446.5 m3/h; variable frequency drive: True | 2 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.well_pump_a
P-031 | source | Well-water pump 2/3 | CentrifugalPump | ar.well | new | capacity fraction: 50 %; design volume flow rate: 446.5 m3/h; variable frequency drive: True | 2 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.well_pump_b
P-032 | source | Well-water pump 3/3 | CentrifugalPump | ar.well | new | capacity fraction: 50 %; design volume flow rate: 446.5 m3/h; variable frequency drive: True | 2 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.well_pump_c
P-033 | source | PAC-loop pump 1/3 | CentrifugalPump | ar.well | new | capacity fraction: 50 %; design volume flow rate: 682.5 m3/h; variable frequency drive: True | 2 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.loop_pump_a
P-034 | source | PAC-loop pump 2/3 | CentrifugalPump | ar.well | new | capacity fraction: 50 %; design volume flow rate: 682.5 m3/h; variable frequency drive: True | 2 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.loop_pump_b
P-035 | source | PAC-loop pump 3/3 | CentrifugalPump | ar.well | new | capacity fraction: 50 %; design volume flow rate: 682.5 m3/h; variable frequency drive: True | 2 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | eq.loop_pump_c
TK-001 | source | Buffer tank – cold water 20 °C | Tank | ar.well | new | operating temperature: 20 °C | 5 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.tank_cold
TK-002 | source | Buffer tank – hot return water 31 °C | Tank | ar.well | new | operating temperature: 31 °C | 5 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.tank_warm
TBD | none | Gas boiler (standby) | Boiler | ar.steam | unspecified |  | 1 | p.3 §4. Logiques de régulation et modes opératoires | eq.boiler
TBD | none | BSST steam user Finisseur | CustomEquipment | ar.bsst | modified | label: Finisseur; steam supply pressure: 4 bar eff. | 1 | p.2 §3. Consommateurs process et modifications | eq.bsst_finisher
TBD | none | BSST steam user Tour ICF (evaporator) | CustomEquipment | ar.bsst | modified | label: Tour ICF; steam supply pressure: 4 bar eff. | 1 | p.2 §3. Consommateurs process et modifications | eq.bsst_icf
TBD | none | Air-preheating hot-water coil (TGE example) | CustomHeatExchanger | ar.bsst | new | air flow rate: 40000 m3/h; air inlet temperature: -15 °C; air outlet temperature: 20 °C; water flow rate: 20769 l/h; water inlet temperature max: 85 °C; water outlet temperature: 65 °C | 2 | p.2 §3. Préchauffage Air Process (BSST) – Exemple Tour TGE | eq.bsst_tge_coil
TBD | none | BSST steam user TGEA | CustomEquipment | ar.bsst | modified | label: TGEA; steam supply pressure: 4 bar eff. | 1 | p.2 §3. Consommateurs process et modifications | eq.bsst_tgea
TBD | none | BSST steam user TGEB | CustomEquipment | ar.bsst | modified | label: TGEB; steam supply pressure: 4 bar eff. | 1 | p.2 §3. Consommateurs process et modifications | eq.bsst_tgeb
TBD | none | CMV stage 1 | CustomCompressor | ar.steam | new | delivery pressure: 1 bar eff.; stage: 1 | 2 | p.1 §1.3 Zone de Production de Vapeur (CMV) | eq.cmv_s1
TBD | none | CMV stage 2 | CustomCompressor | ar.steam | new | delivery pressure: 4 bar eff.; stage: 2 | 2 | p.1 §1.3 Zone de Production de Vapeur (CMV) | eq.cmv_s2
TBD | none | CMV stage 3 | CustomCompressor | ar.steam | new | delivery pressure: 8 bar eff.; minimum technical production: 5.8 t/h; stage: 3 | 2 | p.1 §1.3 Zone de Production de Vapeur (CMV) | eq.cmv_s3
TBD | none | Fermenters CF1-8, CFA, CFB | CustomEquipment | ar.well | modified | members: ['CF1', 'CF2', 'CF3', 'CF4', 'CF5', 'CF6', 'CF7', 'CF8', 'CFA', 'CFB']; required water regime: 20 °C in / 31 °C out | 2 | p.2 §3. Consommateurs process et modifications | eq.fermenters
TBD | none | Flash tank (70 °C) | Vessel | ar.steam | new | operating temperature: 70 °C | 6 | p.1 §1.3 Zone de Production de Vapeur (CMV) | eq.flash_tank
TBD | none | PAC 1A – process heat pump | CustomEquipment | ar.hp | new | arrangement: parallel; cold power: 5.6 MW; cold regime: 31 °C / 20 °C; compressor type: centrifugal; hot power: 8 MW; hot regime: 70 °C / 90 °C; manufacturer: Johnson Controls; refrigerant: R1234ze | 4 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.hp_1a
TBD | none | PAC 1B – process heat pump | CustomEquipment | ar.hp | new | arrangement: parallel; cold power: 5.6 MW; cold regime: 31 °C / 20 °C; compressor type: centrifugal; hot power: 8 MW; hot regime: 70 °C / 90 °C; manufacturer: Johnson Controls; refrigerant: R1234ze | 4 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.hp_1b
TBD | none | PAC 2A – RCUA heat pump | CustomEquipment | ar.hp | new | arrangement: cascade; cold power: 3.8 MW; cold regime: 31 °C / 20 °C; compressor type: centrifugal; hot power: 5.6 MW; hot regime: 85 °C / 105 °C; manufacturer: Johnson Controls; refrigerant: R1233zd/R1234ze | 4 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.hp_2a
TBD | none | PAC 2B – RCUA heat pump | CustomEquipment | ar.hp | new | arrangement: cascade; cold power: 3.8 MW; cold regime: 31 °C / 20 °C; compressor type: centrifugal; hot power: 5.6 MW; hot regime: 85 °C / 105 °C; manufacturer: Johnson Controls; refrigerant: R1233zd/R1234ze | 4 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.hp_2b
TBD | none | PAC 3A – extension heat pump (future) | CustomEquipment | ar.hp | future | arrangement: cascade | 4 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.hp_3a
TBD | none | PAC 3B – extension heat pump (future) | CustomEquipment | ar.hp | future | arrangement: cascade | 4 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.hp_3b
TBD | none | LPF thermal degasser with 44 m³ tank | Vessel | ar.lpf | modified | tank volume: 44 m3 | 5 | p.2 §3. Consommateurs process et modifications | eq.lpf_degasser
TBD | none | New make-up water heater (12 → 80 °C) | PlateHeatExchanger | ar.lpf | new | cold inlet temperature: 12 °C; cold outlet temperature: 80 °C | 4 | p.2 §3. Dégazeur Thermique LPF | eq.lpf_degasser_hx
TBD | none | New hot-water plate exchanger – BACAN1 | PlateHeatExchanger | ar.lpf | new |  | 4 | p.2 §3. Maintien en température (Cuves LPF) | eq.lpf_phx_an1
TBD | none | New hot-water plate exchanger – BACS04 | PlateHeatExchanger | ar.lpf | new |  | 4 | p.2 §3. Maintien en température (Cuves LPF) | eq.lpf_phx_s04
TBD | none | New hot-water plate exchanger – BACS05 | PlateHeatExchanger | ar.lpf | new |  | 4 | p.2 §3. Maintien en température (Cuves LPF) | eq.lpf_phx_s05
TBD | none | Retained steam exchanger (standby) – BACAN1 | CustomHeatExchanger | ar.lpf | existing |  | 4 | p.2 §3. Maintien en température (Cuves LPF) | eq.lpf_shx_an1
TBD | none | Retained steam exchanger (standby) – BACS04 | CustomHeatExchanger | ar.lpf | existing |  | 4 | p.2 §3. Maintien en température (Cuves LPF) | eq.lpf_shx_s04
TBD | none | Retained steam exchanger (standby) – BACS05 | CustomHeatExchanger | ar.lpf | existing |  | 4 | p.2 §3. Maintien en température (Cuves LPF) | eq.lpf_shx_s05
TBD | none | Buffer tank – PAC return 70 °C | Tank | ar.hp | new | operating temperature: 70 °C | 5 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.tank_70
TBD | none | Buffer tank – PAC process supply 90 °C | Tank | ar.hp | new | operating temperature: 90 °C | 5 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.tank_90
TBD | none | Buffer tank – RCUA 85/105 °C | Tank | ar.hp | new | operating temperature: 85 °C / 105 °C | 5 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | eq.tank_rcua

## Line list
Line No. | No. status | Service | From | To | Size | Piping class | Other data | Pieces | Source | Logical line
CW-101 | proposed | Cooling water 20/31 | TK-001 Buffer tank – cold water 20 °C | Fermenters CF1-8, CFA, CFB | ≥DN600 | TBD | temperature: 20 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.017
CW-102 | proposed | Cooling water 20/31 | Fermenters CF1-8, CFA, CFB | Fermenter outlet manifold | ≥DN600 | TBD | temperature: 31 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.018
CW-103 | proposed | Cooling water 20/31 | Fermenter outlet manifold | TK-002 Buffer tank – hot return water 31 °C | ≥DN600 | TBD | temperature: 31 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.019
CW-104 | proposed | Cooling water 20/31 | TK-002 Buffer tank – hot return water 31 °C | PAC-loop pump suction manifold | TBD | TBD | temperature: 31 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.021
CW-105 | proposed | Cooling water 20/31 | PAC-loop pump suction manifold | P-033 PAC-loop pump 1/3 | TBD | TBD | temperature: 31 °C | 2 | rule pump.auxiliaries | ln.022
CW-106 | proposed | Cooling water 20/31 | PAC-loop pump suction manifold | P-034 PAC-loop pump 2/3 | TBD | TBD | temperature: 31 °C | 2 | rule pump.auxiliaries | ln.023
CW-107 | proposed | Cooling water 20/31 | PAC-loop pump suction manifold | P-035 PAC-loop pump 3/3 | TBD | TBD | temperature: 31 °C | 2 | rule pump.auxiliaries | ln.024
CW-108 | proposed | Cooling water 20/31 | P-033 PAC-loop pump 1/3 | PAC-loop pump discharge manifold | TBD | TBD | temperature: 31 °C | 3 | rule pump.auxiliaries | ln.025
CW-109 | proposed | Cooling water 20/31 | P-034 PAC-loop pump 2/3 | PAC-loop pump discharge manifold | TBD | TBD | temperature: 31 °C | 3 | rule pump.auxiliaries | ln.026
CW-110 | proposed | Cooling water 20/31 | P-035 PAC-loop pump 3/3 | PAC-loop pump discharge manifold | TBD | TBD | temperature: 31 °C | 3 | rule pump.auxiliaries | ln.027
CW-111 | proposed | Cooling water 20/31 | PAC-loop pump discharge manifold | Cold-water distribution manifold (evaporators + emergency exchangers) | TBD | TBD | temperature: 31 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.028
CW-112 | proposed | Cooling water 20/31 | Cold-water distribution manifold (evaporators + emergency exchangers) | PAC 1A – process heat pump | TBD | TBD | temperature: 31 °C | 2 | rule mode.isolation | ln.029
CW-113 | proposed | Cooling water 20/31 | Cold-water distribution manifold (evaporators + emergency exchangers) | PAC 1B – process heat pump | TBD | TBD | temperature: 31 °C | 2 | rule mode.isolation | ln.030
CW-114 | proposed | Cooling water 20/31 | Cold-water distribution manifold (evaporators + emergency exchangers) | PAC 2A – RCUA heat pump | TBD | TBD | temperature: 31 °C | 2 | rule mode.isolation | ln.031
CW-115 | proposed | Cooling water 20/31 | Cold-water distribution manifold (evaporators + emergency exchangers) | ECH-030 Emergency plate exchanger 1/3 | TBD | TBD | temperature: 31 °C | 2 | rule mode.isolation | ln.032
CW-116 | proposed | Cooling water 20/31 | Cold-water distribution manifold (evaporators + emergency exchangers) | ECH-031 Emergency plate exchanger 2/3 | TBD | TBD | temperature: 31 °C | 2 | rule mode.isolation | ln.033
CW-117 | proposed | Cooling water 20/31 | Cold-water distribution manifold (evaporators + emergency exchangers) | ECH-032 Emergency plate exchanger 3/3 | TBD | TBD | temperature: 31 °C | 2 | rule mode.isolation | ln.034
CW-118 | proposed | Cooling water 20/31 | PAC 1A – process heat pump | Cold-water collection manifold | TBD | TBD | temperature: 20 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.035
CW-119 | proposed | Cooling water 20/31 | PAC 1B – process heat pump | Cold-water collection manifold | TBD | TBD | temperature: 20 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.036
CW-120 | proposed | Cooling water 20/31 | PAC 2A – RCUA heat pump | Cold-water collection manifold | TBD | TBD | temperature: 20 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.037
CW-121 | proposed | Cooling water 20/31 | ECH-030 Emergency plate exchanger 1/3 | Cold-water collection manifold | TBD | TBD | temperature: 20 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.038
CW-122 | proposed | Cooling water 20/31 | ECH-031 Emergency plate exchanger 2/3 | Cold-water collection manifold | TBD | TBD | temperature: 20 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.039
CW-123 | proposed | Cooling water 20/31 | ECH-032 Emergency plate exchanger 3/3 | Cold-water collection manifold | TBD | TBD | temperature: 20 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.040
CW-124 | proposed | Cooling water 20/31 | Cold-water collection manifold | TK-001 Buffer tank – cold water 20 °C | TBD | TBD | temperature: 20 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.041
FS-101 | proposed | Flash steam | Flash tank (70 °C) | CMV stage 1 | TBD | TBD |  | 1 | p.1 §1.3 Zone de Production de Vapeur (CMV) | ln.061
HR-101 | proposed | Hot water RCUA 85/105 | Buffer tank – RCUA 85/105 °C | PAC 2B – RCUA heat pump | TBD | TBD | temperature: 85 °C | 1 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | ln.059
HR-102 | proposed | Hot water RCUA 85/105 | RCUA network – return 85 °C (placeholder battery limit) | Buffer tank – RCUA 85/105 °C | TBD | TBD | temperature: 85 °C | 1 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | ln.060
HR-103 | proposed | Hot water RCUA 85/105 | PAC 2B – RCUA heat pump | RCUA network – supply 105 °C (placeholder battery limit) | TBD | TBD | temperature: 105 °C | 1 | p.1 §1.2 Zone de Production de Chaleur (PAC) et Stockage | ln.h105
HS-101 | proposed | Steam 8 bar | CMV stage 3 | 8 bar header junction | DN150 | TBD | nominal flow: 1.2 t/h; pressure: 8 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.068
HS-102 | proposed | Steam 8 bar | 8 bar header split | Réseau BSST (8 bar eff.) | DN150 | TBD | nominal flow: 1.2 t/h; pressure: 8 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.069
HS-103 | proposed | Steam 8 bar | Gas boiler (standby) | PCV-104 Boiler back-up pressure control valve (PCV) | TBD | TBD |  | 4 | rule control_valve.manifold | ln.070
HS-104 | proposed | Steam 8 bar | PCV-104 Boiler back-up pressure control valve (PCV) | 8 bar header junction | TBD | TBD |  | 3 | rule control_valve.manifold | ln.071
HS-105 | proposed | Steam 8 bar | 8 bar header split | PCV-502 Overproduction spill valve 8 → 4 bar (PCV) | TBD | TBD |  | 4 | rule control_valve.manifold | ln.072
HS-106 | proposed | Steam 8 bar | Bypass split – Boiler back-up pressure control valve (PCV) | XV-223 Bypass globe valve – Boiler back-up pressure control valve (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_boiler.byp_in
HS-107 | proposed | Steam 8 bar | XV-223 Bypass globe valve – Boiler back-up pressure control valve (PCV) | Bypass merge – Boiler back-up pressure control valve (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_boiler.byp_out
HS-108 | proposed | Steam 8 bar | Purge tee – Boiler back-up pressure control valve (PCV) | XV-226 Purge valve – Boiler back-up pressure control valve (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_boiler.purge
HS-109 | proposed | Steam 8 bar | Bypass split – Overproduction spill valve 8 → 4 bar (PCV) | XV-231 Bypass globe valve – Overproduction spill valve 8 → 4 bar (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_spill_8_4.byp_in
HS-110 | proposed | Steam 8 bar | XV-231 Bypass globe valve – Overproduction spill valve 8 → 4 bar (PCV) | Bypass merge – Overproduction spill valve 8 → 4 bar (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_spill_8_4.byp_out
HS-111 | proposed | Steam 8 bar | Purge tee – Overproduction spill valve 8 → 4 bar (PCV) | XV-234 Purge valve – Overproduction spill valve 8 → 4 bar (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_spill_8_4.purge
HS-112 | proposed | Steam 8 bar | 8 bar header junction | 8 bar header split | DN150 | TBD | nominal flow: 1.2 t/h; pressure: 8 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.h8
HW-101 | proposed | Hot water 90/70 | Buffer tank – PAC return 70 °C | PAC 1A/1B condenser inlet manifold | DN200–350 | TBD | temperature: 70 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.042
HW-102 | proposed | Hot water 90/70 | PAC 1A/1B condenser inlet manifold | PAC 1A – process heat pump | DN200–350 | TBD | temperature: 70 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.043
HW-103 | proposed | Hot water 90/70 | PAC 1A/1B condenser inlet manifold | PAC 1B – process heat pump | DN200–350 | TBD | temperature: 70 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.044
HW-104 | proposed | Hot water 90/70 | PAC 1A – process heat pump | PAC 1A/1B condenser outlet manifold | DN200–350 | TBD | temperature: 90 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.045
HW-105 | proposed | Hot water 90/70 | PAC 1B – process heat pump | PAC 1A/1B condenser outlet manifold | DN200–350 | TBD | temperature: 90 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.046
HW-106 | proposed | Hot water 90/70 | PAC 1A/1B condenser outlet manifold | Buffer tank – PAC process supply 90 °C | DN200–350 | TBD | temperature: 90 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.047
HW-107 | proposed | Hot water 90/70 | Hot-water 90 °C distribution manifold | New hot-water plate exchanger – BACS04 | DN200–350 | TBD | temperature: 90 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.048
HW-108 | proposed | Hot water 90/70 | Hot-water 90 °C distribution manifold | New hot-water plate exchanger – BACAN1 | DN200–350 | TBD | temperature: 90 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.049
HW-109 | proposed | Hot water 90/70 | Hot-water 90 °C distribution manifold | New hot-water plate exchanger – BACS05 | DN200–350 | TBD | temperature: 90 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.050
HW-110 | proposed | Hot water 90/70 | Hot-water 90 °C distribution manifold | Air-preheating hot-water coil (TGE example) | DN200–350 | TBD | temperature: 90 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.051
HW-111 | proposed | Hot water 90/70 | Hot-water 90 °C distribution manifold | Flash tank (70 °C) | DN200–350 | TBD | temperature: 90 °C | 1 | p.1 §1.3 Zone de Production de Vapeur (CMV) | ln.052
HW-112 | proposed | Hot water 90/70 | New hot-water plate exchanger – BACS04 | Hot-water return manifold | DN200–350 | TBD | temperature: 70 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.053
HW-113 | proposed | Hot water 90/70 | New hot-water plate exchanger – BACAN1 | Hot-water return manifold | DN200–350 | TBD | temperature: 70 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.054
HW-114 | proposed | Hot water 90/70 | New hot-water plate exchanger – BACS05 | Hot-water return manifold | DN200–350 | TBD | temperature: 70 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.055
HW-115 | proposed | Hot water 90/70 | Air-preheating hot-water coil (TGE example) | Hot-water return manifold | DN200–350 | TBD | temperature: 70 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.056
HW-116 | proposed | Hot water 90/70 | Hot-water return manifold | Buffer tank – PAC return 70 °C | DN200–350 | TBD | temperature: 70 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.057
HW-117 | proposed | Hot water 90/70 | Buffer tank – PAC process supply 90 °C | Hot-water 90 °C distribution manifold | DN200–350 | TBD | temperature: 90 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.hw90
IL-101 | proposed | Internal loop PAC 2A/2B 55/50 | PAC 2B – RCUA heat pump | PAC 2A – RCUA heat pump | TBD | TBD | temperature return: 50 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.058
IL-102 | proposed | Internal loop PAC 2A/2B 55/50 | PAC 2A – RCUA heat pump | PAC 2B – RCUA heat pump | TBD | TBD | temperature return: 50 °C; temperature supply: 55 °C | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.pac2_internal
LS-101 | proposed | Steam 1 bar | CMV stage 1 | CMV stage 1 outlet manifold | TBD | TBD |  | 1 | p.1 §1.3 Zone de Production de Vapeur (CMV) | ln.062
LS-102 | proposed | Steam 1 bar | CMV stage 1 outlet manifold | CMV stage 2 | TBD | TBD |  | 1 | p.1 §1.3 Zone de Production de Vapeur (CMV) | ln.063
LS-103 | proposed | Steam 1 bar | CMV stage 1 outlet manifold | 1 bar header junction | DN200 | TBD | nominal flow: 2.9 t/h; pressure: 1 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.064
LS-104 | proposed | Steam 1 bar | PCV-501 Overproduction spill valve 4 → 1 bar (PCV) | 1 bar header junction | TBD | TBD |  | 3 | rule control_valve.manifold | ln.075
LS-105 | proposed | Steam 1 bar | 1 bar header junction | Réseau BSST Nord (1 bar eff.) | DN200 | TBD | nominal flow: 2.9 t/h; pressure: 1 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.h1
MS-101 | proposed | Steam 4 bar | CMV stage 2 | CMV stage 2 outlet manifold | TBD | TBD |  | 1 | p.1 §1.3 Zone de Production de Vapeur (CMV) | ln.065
MS-102 | proposed | Steam 4 bar | CMV stage 2 outlet manifold | CMV stage 3 | TBD | TBD |  | 1 | p.1 §1.3 Zone de Production de Vapeur (CMV) | ln.066
MS-103 | proposed | Steam 4 bar | CMV stage 2 outlet manifold | 4 bar header junction | DN300 | TBD | nominal flow: 9.1 t/h; pressure: 4 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.067
MS-104 | proposed | Steam 4 bar | PCV-502 Overproduction spill valve 8 → 4 bar (PCV) | 4 bar header junction | TBD | TBD |  | 3 | rule control_valve.manifold | ln.073
MS-105 | proposed | Steam 4 bar | 4 bar header split | PCV-501 Overproduction spill valve 4 → 1 bar (PCV) | TBD | TBD |  | 4 | rule control_valve.manifold | ln.074
MS-106 | proposed | Steam 4 bar | 4 bar header split | LPF 4 bar steam network | DN300 | TBD | nominal flow: 9.1 t/h; pressure: 4 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.076
MS-107 | proposed | Steam 4 bar | 4 bar header split | BSST Sud 4 bar steam network | DN300 | TBD | nominal flow: 9.1 t/h; pressure: 4 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.077
MS-108 | proposed | Steam 4 bar | LPF 4 bar steam network | K3 LPF steam user K3 | TBD | TBD |  | 1 | p.2 §3. Consommateurs process et modifications | ln.078
MS-109 | proposed | Steam 4 bar | LPF 4 bar steam network | MESSO LPF steam user MESSO | TBD | TBD |  | 1 | p.2 §3. Consommateurs process et modifications | ln.079
MS-110 | proposed | Steam 4 bar | LPF 4 bar steam network | GEA LPF steam user GEA | TBD | TBD |  | 1 | p.2 §3. Consommateurs process et modifications | ln.080
MS-111 | proposed | Steam 4 bar | BSST Sud 4 bar steam network | BSST steam user TGEA | TBD | TBD |  | 1 | p.2 §3. Consommateurs process et modifications | ln.081
MS-112 | proposed | Steam 4 bar | BSST Sud 4 bar steam network | BSST steam user TGEB | TBD | TBD |  | 1 | p.2 §3. Consommateurs process et modifications | ln.082
MS-113 | proposed | Steam 4 bar | BSST Sud 4 bar steam network | BSST steam user Finisseur | TBD | TBD |  | 1 | p.2 §3. Consommateurs process et modifications | ln.083
MS-114 | proposed | Steam 4 bar | BSST Sud 4 bar steam network | BSST steam user Tour ICF (evaporator) | TBD | TBD |  | 1 | p.2 §3. Consommateurs process et modifications | ln.084
MS-115 | proposed | Steam 4 bar | Bypass split – Overproduction spill valve 4 → 1 bar (PCV) | XV-227 Bypass globe valve – Overproduction spill valve 4 → 1 bar (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_spill_4_1.byp_in
MS-116 | proposed | Steam 4 bar | XV-227 Bypass globe valve – Overproduction spill valve 4 → 1 bar (PCV) | Bypass merge – Overproduction spill valve 4 → 1 bar (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_spill_4_1.byp_out
MS-117 | proposed | Steam 4 bar | Purge tee – Overproduction spill valve 4 → 1 bar (PCV) | XV-230 Purge valve – Overproduction spill valve 4 → 1 bar (PCV) | TBD | TBD |  | 1 | rule control_valve.manifold | ln.gen.pcv_spill_4_1.purge
MS-118 | proposed | Steam 4 bar | 4 bar header junction | 4 bar header split | DN300 | TBD | nominal flow: 9.1 t/h; pressure: 4 bar eff. | 1 | p.2 §2. Lignes principales et réseaux de distribution | ln.h4
PF-101 | proposed | Process fluid (LPF tank) | BACS04 LPF tank BACS04 | Tank S04 heating-loop split | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.085
PF-102 | proposed | Process fluid (LPF tank) | Tank S04 heating-loop split | New hot-water plate exchanger – BACS04 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.086
PF-103 | proposed | Process fluid (LPF tank) | Tank S04 heating-loop split | Retained steam exchanger (standby) – BACS04 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.087
PF-104 | proposed | Process fluid (LPF tank) | New hot-water plate exchanger – BACS04 | Tank S04 heating-loop merge | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.088
PF-105 | proposed | Process fluid (LPF tank) | Retained steam exchanger (standby) – BACS04 | Tank S04 heating-loop merge | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.089
PF-106 | proposed | Process fluid (LPF tank) | Tank S04 heating-loop merge | BACS04 LPF tank BACS04 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.090
PF-107 | proposed | Process fluid (LPF tank) | BACAN1 LPF tank BACAN1 | Tank AN1 heating-loop split | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.091
PF-108 | proposed | Process fluid (LPF tank) | Tank AN1 heating-loop split | New hot-water plate exchanger – BACAN1 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.092
PF-109 | proposed | Process fluid (LPF tank) | Tank AN1 heating-loop split | Retained steam exchanger (standby) – BACAN1 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.093
PF-110 | proposed | Process fluid (LPF tank) | New hot-water plate exchanger – BACAN1 | Tank AN1 heating-loop merge | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.094
PF-111 | proposed | Process fluid (LPF tank) | Retained steam exchanger (standby) – BACAN1 | Tank AN1 heating-loop merge | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.095
PF-112 | proposed | Process fluid (LPF tank) | Tank AN1 heating-loop merge | BACAN1 LPF tank BACAN1 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.096
PF-113 | proposed | Process fluid (LPF tank) | BACS05 LPF tank BACS05 | Tank S05 heating-loop split | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.097
PF-114 | proposed | Process fluid (LPF tank) | Tank S05 heating-loop split | New hot-water plate exchanger – BACS05 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.098
PF-115 | proposed | Process fluid (LPF tank) | Tank S05 heating-loop split | Retained steam exchanger (standby) – BACS05 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.099
PF-116 | proposed | Process fluid (LPF tank) | New hot-water plate exchanger – BACS05 | Tank S05 heating-loop merge | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.100
PF-117 | proposed | Process fluid (LPF tank) | Retained steam exchanger (standby) – BACS05 | Tank S05 heating-loop merge | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.101
PF-118 | proposed | Process fluid (LPF tank) | Tank S05 heating-loop merge | BACS05 LPF tank BACS05 | TBD | TBD |  | 1 | p.2 §3. Maintien en température (Cuves LPF) | ln.102
TW-101 | proposed | Treated make-up water | Treated make-up water (Eau Traitée, 12 °C) | New make-up water heater (12 → 80 °C) | TBD | TBD | temperature: 12 °C | 1 | p.2 §3. Dégazeur Thermique LPF | ln.103
TW-102 | proposed | Treated make-up water | New make-up water heater (12 → 80 °C) | LPF thermal degasser with 44 m³ tank | TBD | TBD | temperature: 80 °C | 1 | p.2 §3. Dégazeur Thermique LPF | ln.104
WW-101 | proposed | Well water | Puits 3 – well water source (12 °C) | Well-pump suction manifold | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.001
WW-102 | proposed | Well water | Well-pump suction manifold | P-030 Well-water pump 1/3 | TBD | TBD |  | 2 | rule pump.auxiliaries | ln.002
WW-103 | proposed | Well water | Well-pump suction manifold | P-031 Well-water pump 2/3 | TBD | TBD |  | 2 | rule pump.auxiliaries | ln.003
WW-104 | proposed | Well water | Well-pump suction manifold | P-032 Well-water pump 3/3 | TBD | TBD |  | 2 | rule pump.auxiliaries | ln.004
WW-105 | proposed | Well water | P-030 Well-water pump 1/3 | Well-pump discharge manifold | TBD | TBD |  | 3 | rule pump.auxiliaries | ln.005
WW-106 | proposed | Well water | P-031 Well-water pump 2/3 | Well-pump discharge manifold | TBD | TBD |  | 3 | rule pump.auxiliaries | ln.006
WW-107 | proposed | Well water | P-032 Well-water pump 3/3 | Well-pump discharge manifold | TBD | TBD |  | 3 | rule pump.auxiliaries | ln.007
WW-108 | proposed | Well water | Well-pump discharge manifold | Emergency-exchanger well-water inlet manifold | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.008
WW-109 | proposed | Well water | Emergency-exchanger well-water inlet manifold | ECH-030 Emergency plate exchanger 1/3 | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.009
WW-110 | proposed | Well water | Emergency-exchanger well-water inlet manifold | ECH-031 Emergency plate exchanger 2/3 | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.010
WW-111 | proposed | Well water | Emergency-exchanger well-water inlet manifold | ECH-032 Emergency plate exchanger 3/3 | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.011
WW-112 | proposed | Well water | ECH-030 Emergency plate exchanger 1/3 | Emergency-exchanger well-water outlet manifold | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.012
WW-113 | proposed | Well water | ECH-031 Emergency plate exchanger 2/3 | Emergency-exchanger well-water outlet manifold | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.013
WW-114 | proposed | Well water | ECH-032 Emergency plate exchanger 3/3 | Emergency-exchanger well-water outlet manifold | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.014
WW-115 | proposed | Well water | Emergency-exchanger well-water outlet manifold | DARSE discharge manifold | TBD | TBD |  | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.015
WW-116 | proposed | Well water | DARSE discharge manifold | Rejet vers DARSE (< 30 °C) | TBD | TBD | temperature max: 30 °C | 1 | p.1 §1.1 Zone de Captage et Boucle Fermenteurs | ln.016
WW-117 | proposed | Well water | Fermenter outlet manifold | DARSE discharge manifold | TBD | TBD |  | 1 | p.3 §4. Logiques de régulation et modes opératoires | ln.020
| none | Drain (Hot water 90/70) | Flash tank (70 °C) | XV-204 Drain valve – Flash tank (70 °C) | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.flash_tank.drain
| none | Vent (Hot water 90/70) | Flash tank (70 °C) | XV-205 Vent valve – Flash tank (70 °C) | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.flash_tank.vent
| none | Drain (Treated make-up water) | LPF thermal degasser with 44 m³ tank | XV-215 Drain valve – LPF thermal degasser with 44 m³ tank | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.lpf_degasser.drain
| none | Vent (Treated make-up water) | LPF thermal degasser with 44 m³ tank | XV-216 Vent valve – LPF thermal degasser with 44 m³ tank | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.lpf_degasser.vent
| none | Drain (Process fluid (LPF tank)) | BACAN1 LPF tank BACAN1 | XV-217 Drain valve – BACAN1 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.lpf_tank_an1.drain
| none | Vent (Process fluid (LPF tank)) | BACAN1 LPF tank BACAN1 | XV-218 Vent valve – BACAN1 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.lpf_tank_an1.vent
| none | Drain (Process fluid (LPF tank)) | BACS04 LPF tank BACS04 | XV-219 Drain valve – BACS04 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.lpf_tank_s04.drain
| none | Vent (Process fluid (LPF tank)) | BACS04 LPF tank BACS04 | XV-220 Vent valve – BACS04 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.lpf_tank_s04.vent
| none | Drain (Process fluid (LPF tank)) | BACS05 LPF tank BACS05 | XV-221 Drain valve – BACS05 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.lpf_tank_s05.drain
| none | Vent (Process fluid (LPF tank)) | BACS05 LPF tank BACS05 | XV-222 Vent valve – BACS05 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.lpf_tank_s05.vent
| none | Drain (Hot water 90/70) | Buffer tank – PAC return 70 °C | XV-235 Drain valve – Buffer tank – PAC return 70 °C | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_70.drain
| none | Vent (Hot water 90/70) | Buffer tank – PAC return 70 °C | XV-236 Vent valve – Buffer tank – PAC return 70 °C | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_70.vent
| none | Drain (Hot water 90/70) | Buffer tank – PAC process supply 90 °C | XV-237 Drain valve – Buffer tank – PAC process supply 90 °C | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_90.drain
| none | Vent (Hot water 90/70) | Buffer tank – PAC process supply 90 °C | XV-238 Vent valve – Buffer tank – PAC process supply 90 °C | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_90.vent
| none | Drain (Cooling water 20/31) | TK-001 Buffer tank – cold water 20 °C | XV-239 Drain valve – TK-001 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_cold.drain
| none | Vent (Cooling water 20/31) | TK-001 Buffer tank – cold water 20 °C | XV-240 Vent valve – TK-001 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_cold.vent
| none | Drain (Hot water RCUA 85/105) | Buffer tank – RCUA 85/105 °C | XV-241 Drain valve – Buffer tank – RCUA 85/105 °C | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_rcua.drain
| none | Vent (Hot water RCUA 85/105) | Buffer tank – RCUA 85/105 °C | XV-242 Vent valve – Buffer tank – RCUA 85/105 °C | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_rcua.vent
| none | Drain (Cooling water 20/31) | TK-002 Buffer tank – hot return water 31 °C | XV-243 Drain valve – TK-002 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_warm.drain
| none | Vent (Cooling water 20/31) | TK-002 Buffer tank – hot return water 31 °C | XV-244 Vent valve – TK-002 | TBD | TBD |  | 1 | rule vessel.auxiliaries | ln.gen.tank_warm.vent

## Valve list
Tag | Function | DEXPI class | Technology | Operation | Line | Open end | Status | Source | Topology id
NRV-251 | check | CheckValve | check | unknown | CW-108 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_a.discharge_check
NRV-252 | check | CheckValve | check | unknown | CW-109 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_b.discharge_check
NRV-253 | check | CheckValve | check | unknown | CW-110 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_c.discharge_check
NRV-254 | check | CheckValve | check | unknown | WW-105 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_a.discharge_check
NRV-255 | check | CheckValve | check | unknown | WW-106 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_b.discharge_check
NRV-256 | check | CheckValve | check | unknown | WW-107 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_c.discharge_check
PCV-104 | control | CustomOperatedValve | to be selected | automated | HS-103 |  | specification | p.3 §4. Logiques de régulation et modes opératoires | pc.pcv_boiler
PCV-501 | control | CustomOperatedValve | to be selected | automated | MS-105 |  | specification | p.3 §4. Logiques de régulation et modes opératoires | pc.pcv_spill_4_1
PCV-502 | control | CustomOperatedValve | to be selected | automated | HS-105 |  | specification | p.3 §4. Logiques de régulation et modes opératoires | pc.pcv_spill_8_4
XV-201 | isolation | CustomOperatedValve | to be selected | unknown | CW-115 |  | proposed – pending review | rule mode.isolation | pc.gen.emerg_hx_a.hot_in_isolation
XV-202 | isolation | CustomOperatedValve | to be selected | unknown | CW-116 |  | proposed – pending review | rule mode.isolation | pc.gen.emerg_hx_b.hot_in_isolation
XV-203 | isolation | CustomOperatedValve | to be selected | unknown | CW-117 |  | proposed – pending review | rule mode.isolation | pc.gen.emerg_hx_c.hot_in_isolation
XV-204 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.flash_tank.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.flash_tank.drain
XV-205 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.flash_tank.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.flash_tank.vent
XV-206 | isolation | CustomOperatedValve | to be selected | unknown | CW-112 |  | proposed – pending review | rule mode.isolation | pc.gen.hp_1a.evap_in_isolation
XV-207 | isolation | CustomOperatedValve | to be selected | unknown | CW-113 |  | proposed – pending review | rule mode.isolation | pc.gen.hp_1b.evap_in_isolation
XV-208 | isolation | CustomOperatedValve | to be selected | unknown | CW-114 |  | proposed – pending review | rule mode.isolation | pc.gen.hp_2a.evap_in_isolation
XV-209 | isolation | CustomOperatedValve | to be selected | manual | CW-108 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_a.discharge_isolation
XV-210 | isolation | CustomOperatedValve | to be selected | manual | CW-105 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_a.suction_isolation
XV-211 | isolation | CustomOperatedValve | to be selected | manual | CW-109 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_b.discharge_isolation
XV-212 | isolation | CustomOperatedValve | to be selected | manual | CW-106 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_b.suction_isolation
XV-213 | isolation | CustomOperatedValve | to be selected | manual | CW-110 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_c.discharge_isolation
XV-214 | isolation | CustomOperatedValve | to be selected | manual | CW-107 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.loop_pump_c.suction_isolation
XV-215 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.lpf_degasser.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.lpf_degasser.drain
XV-216 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.lpf_degasser.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.lpf_degasser.vent
XV-217 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.lpf_tank_an1.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.lpf_tank_an1.drain
XV-218 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.lpf_tank_an1.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.lpf_tank_an1.vent
XV-219 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.lpf_tank_s04.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.lpf_tank_s04.drain
XV-220 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.lpf_tank_s04.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.lpf_tank_s04.vent
XV-221 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.lpf_tank_s05.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.lpf_tank_s05.drain
XV-222 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.lpf_tank_s05.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.lpf_tank_s05.vent
XV-223 | bypass | GlobeValve | globe | unknown | HS-106 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_boiler.byp_valve
XV-224 | isolation | CustomOperatedValve | to be selected | unknown | HS-104 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_boiler.iso_dn
XV-225 | isolation | CustomOperatedValve | to be selected | unknown | HS-103 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_boiler.iso_up
XV-226 | purge | CustomOperatedValve | to be selected | unknown | HS-108 | drain | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_boiler.purge
XV-227 | bypass | GlobeValve | globe | unknown | MS-115 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_spill_4_1.byp_valve
XV-228 | isolation | CustomOperatedValve | to be selected | unknown | LS-104 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_spill_4_1.iso_dn
XV-229 | isolation | CustomOperatedValve | to be selected | unknown | MS-105 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_spill_4_1.iso_up
XV-230 | purge | CustomOperatedValve | to be selected | unknown | MS-117 | drain | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_spill_4_1.purge
XV-231 | bypass | GlobeValve | globe | unknown | HS-109 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_spill_8_4.byp_valve
XV-232 | isolation | CustomOperatedValve | to be selected | unknown | MS-104 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_spill_8_4.iso_dn
XV-233 | isolation | CustomOperatedValve | to be selected | unknown | HS-105 |  | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_spill_8_4.iso_up
XV-234 | purge | CustomOperatedValve | to be selected | unknown | HS-111 | drain | proposed – pending review | rule control_valve.manifold | pc.gen.pcv_spill_8_4.purge
XV-235 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.tank_70.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_70.drain
XV-236 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.tank_70.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_70.vent
XV-237 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.tank_90.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_90.drain
XV-238 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.tank_90.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_90.vent
XV-239 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.tank_cold.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_cold.drain
XV-240 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.tank_cold.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_cold.vent
XV-241 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.tank_rcua.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_rcua.drain
XV-242 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.tank_rcua.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_rcua.vent
XV-243 | drain | CustomOperatedValve | to be selected | unknown | ln.gen.tank_warm.drain | drain | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_warm.drain
XV-244 | vent | CustomOperatedValve | to be selected | unknown | ln.gen.tank_warm.vent | vent | proposed – pending review | rule vessel.auxiliaries | pc.gen.tank_warm.vent
XV-245 | isolation | CustomOperatedValve | to be selected | manual | WW-105 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_a.discharge_isolation
XV-246 | isolation | CustomOperatedValve | to be selected | manual | WW-102 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_a.suction_isolation
XV-247 | isolation | CustomOperatedValve | to be selected | manual | WW-106 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_b.discharge_isolation
XV-248 | isolation | CustomOperatedValve | to be selected | manual | WW-103 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_b.suction_isolation
XV-249 | isolation | CustomOperatedValve | to be selected | manual | WW-107 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_c.discharge_isolation
XV-250 | isolation | CustomOperatedValve | to be selected | manual | WW-104 |  | proposed – pending review | rule pump.auxiliaries | pc.gen.well_pump_c.suction_isolation

## Instrument index
Tag | ISA code | Variable | Function | Location / line | Loop | Range | Alarm / trip | Status | Source | Topology id
LT-401 | LT | level | transmitter | Flash tank (70 °C) |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.flash_tank.lt
LT-402 | LT | level | transmitter | LPF thermal degasser with 44 m³ tank |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.lpf_degasser.lt
LT-403 | LT | level | transmitter | BACAN1 LPF tank BACAN1 |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.lpf_tank_an1.lt
LT-404 | LT | level | transmitter | BACS04 LPF tank BACS04 |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.lpf_tank_s04.lt
LT-405 | LT | level | transmitter | BACS05 LPF tank BACS05 |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.lpf_tank_s05.lt
LT-406 | LT | level | transmitter | Buffer tank – PAC return 70 °C |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.tank_70.lt
LT-407 | LT | level | transmitter | Buffer tank – PAC process supply 90 °C |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.tank_90.lt
LT-408 | LT | level | transmitter | TK-001 Buffer tank – cold water 20 °C |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.tank_cold.lt
LT-409 | LT | level | transmitter | Buffer tank – RCUA 85/105 °C |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.tank_rcua.lt
LT-410 | LT | level | transmitter | TK-002 Buffer tank – hot return water 31 °C |  | TBD | TBD | proposed – pending review | rule vessel.auxiliaries | in.tank_warm.lt
PIC-104 | PIC | pressure | controller |  | loop.boiler_backup | TBD | TBD | proposed – pending review | rule control_loop.from_requirement | in.boiler_backup.pic
PT-101 | PT | pressure | transmitter | LS-105 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.h1.pt
PT-102 | PT | pressure | transmitter | HR-103 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.h105.pt
PT-103 | PT | pressure | transmitter | MS-118 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.h4.pt
PT-104 | PT | pressure | transmitter | HS-112 | loop.boiler_backup | TBD | TBD | proposed – pending review | rule header.instrumentation | in.h8.pt
PT-105 | PT | pressure | transmitter | HW-117 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.hw90.pt
TT-301 | TT | temperature | transmitter | LS-105 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.h1.tt
TT-302 | TT | temperature | transmitter | HR-103 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.h105.tt
TT-303 | TT | temperature | transmitter | MS-118 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.h4.tt
TT-304 | TT | temperature | transmitter | HS-112 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.h8.tt
TT-305 | TT | temperature | transmitter | HW-117 |  | TBD | TBD | proposed – pending review | rule header.instrumentation | in.hw90.tt

## Holds
Hold | Decision | Drawn today | Question | Affects | Answer | Open point
H1 | Emergency exchangers ECH-030..032 – parallel or series? | Parallel branch of the cooling-water loop, beside the heat-pump evaporators. | Confirm parallel arrangement and the well-water path in Normal mode. | eq.emerg_hx_a, eq.emerg_hx_b, eq.emerg_hx_c, mf.cw_s, mf.cw_m |  | ur.ech_position
H2 | PAC 2A/2B – physical cascade? | 2A condenser feeds the 2B evaporator through the 55/50 °C internal loop; only 2B delivers 85/105 °C to RCUA. | Confirm the 2A/2B cascade connections. | eq.hp_2a, eq.hp_2b, ln.pac2_internal |  | ur.cascade_2a_2b
H3 | Circulation pumps of the fermenter leg and hot-water loops | Only P-033..035 (TK-002 outlet). No other pump drawn – the specification names none. | Where are the circulation pumps of the fermenter leg and of the hot-water loops? | eq.loop_pump_a, eq.loop_pump_b, eq.loop_pump_c, eq.tank_cold, eq.tank_70, eq.tank_90, eq.tank_rcua |  | ur.loop_pump_position
H4 | RCUA buffer – one tank or one per temperature level? | One RCUA buffer tank (85/105 °C). | One RCUA tank or one per temperature level? | eq.tank_rcua |  | ur.tank_count
H5 | Spill valves 8→4 and 4→1 bar – control philosophy | Control valves with manifolds, no control loop (variable, setpoint and fail position not given). | Control philosophy of the overproduction cascade. | pc.pcv_spill_8_4, pc.pcv_spill_4_1, cr.spill_8_4, cr.spill_4_1 |  | ur.spill_control
H6 | Flash tank – liquid destination and CMV staging | Flash vapour → CMV stages 1-2-3 in series; 70 °C liquid outlet left open. | Flash-tank liquid destination and pressure; confirm series staging. | eq.flash_tank, eq.cmv_s1, eq.cmv_s2, eq.cmv_s3 |  | ur.flash_tank
H7 | Air-preheating coil – 85 °C limit on a 90 °C header | One coil (TGE example) fed directly from the 90/70 °C header; no tempering arrangement. | How is the 85 °C inlet limit achieved, and how many coils are needed? | eq.bsst_tge_coil, ln.hw90 |  | ur.tge_coil
H8 | Thermal degasser – 4 bar or 1 bar steam? | Steam inlet left unconnected. | Select 4 bar or 1 bar for the degasser. | eq.lpf_degasser |  | ur.degasser_steam
H9 | Make-up water heater (12→80 °C) – heating medium | Hot side left open. | Heating medium of the make-up heater. | eq.lpf_degasser_hx |  | ur.degasser_hx_medium
H10 | LPF tank heating loops – pump and steam supply | Plate exchangers on the tank loops; retained steam exchangers on standby with open steam/condensate nozzles. |  | eq.lpf_shx_s04, eq.lpf_shx_an1, eq.lpf_shx_s05 |  | ur.lpf_tank_loops
H11 | Ultimate mode – well-water feed to the fermenters | Only the post-fermenter discharge to DARSE is drawn. |  | mode.ultimate, mf.ferm_out |  | ur.ultimate_feed
H12 | Hot-water networks – local steam back-up equipment | Not drawn (not described). |  | mode.emergency_hx |  | ur.hw_backup
H13 | RCUA network battery limits | Placeholder battery-limit flags for the 105 °C supply and 85 °C return. |  | bc.rcua_out, bc.rcua_return |  | ur.rcua_limits
H14 | Valve technology of the generic valves | Generic valve symbol, DEXPI CustomOperatedValve 'technology to be selected'. | Select the valve technology for each valve function. | pc.gen.emerg_hx_a.hot_in_isolation, pc.gen.emerg_hx_b.hot_in_isolation, pc.gen.emerg_hx_c.hot_in_isolation, pc.gen.flash_tank.drain, pc.gen.flash_tank.vent, pc.gen.hp_1a.evap_in_isolation, pc.gen.hp_1b.evap_in_isolation, pc.gen.hp_2a.evap_in_isolation, pc.gen.loop_pump_a.discharge_isolation, pc.gen.loop_pump_a.suction_isolation, pc.gen.loop_pump_b.discharge_isolation, pc.gen.loop_pump_b.suction_isolation, pc.gen.loop_pump_c.discharge_isolation, pc.gen.loop_pump_c.suction_isolation, pc.gen.lpf_degasser.drain, pc.gen.lpf_degasser.vent, pc.gen.lpf_tank_an1.drain, pc.gen.lpf_tank_an1.vent, pc.gen.lpf_tank_s04.drain, pc.gen.lpf_tank_s04.vent, pc.gen.lpf_tank_s05.drain, pc.gen.lpf_tank_s05.vent, pc.gen.pcv_boiler.iso_dn, pc.gen.pcv_boiler.iso_up, pc.gen.pcv_boiler.purge, pc.gen.pcv_spill_4_1.iso_dn, pc.gen.pcv_spill_4_1.iso_up, pc.gen.pcv_spill_4_1.purge, pc.gen.pcv_spill_8_4.iso_dn, pc.gen.pcv_spill_8_4.iso_up, pc.gen.pcv_spill_8_4.purge, pc.gen.tank_70.drain, pc.gen.tank_70.vent, pc.gen.tank_90.drain, pc.gen.tank_90.vent, pc.gen.tank_cold.drain, pc.gen.tank_cold.vent, pc.gen.tank_rcua.drain, pc.gen.tank_rcua.vent, pc.gen.tank_warm.drain, pc.gen.tank_warm.vent, pc.gen.well_pump_a.discharge_isolation, pc.gen.well_pump_a.suction_isolation, pc.gen.well_pump_b.discharge_isolation, pc.gen.well_pump_b.suction_isolation, pc.gen.well_pump_c.discharge_isolation, pc.gen.well_pump_c.suction_isolation, pc.pcv_boiler, pc.pcv_spill_4_1, pc.pcv_spill_8_4 |  | ur.gen.valve_technology

## Rule approvals
Rule | Pending objects | Adds | Command
control_loop.from_requirement | 4 | 2 × Signal, 1 × Instrument, 1 × ControlLoop | pid review <project> --approve-rule control_loop.from_requirement
control_valve.manifold | 51 | 30 × ProcessLine, 21 × Component | pid review <project> --approve-rule control_valve.manifold
header.instrumentation | 10 | 10 × Instrument | pid review <project> --approve-rule header.instrumentation
lines.numbering | 86 | 86 × line_number on a source object | pid review <project> --approve-rule lines.numbering
mode.isolation | 18 | 12 × ProcessLine, 6 × Component | pid review <project> --approve-rule mode.isolation
pump.auxiliaries | 48 | 30 × ProcessLine, 18 × Component | pid review <project> --approve-rule pump.auxiliaries
tagging.isa | 3 | 3 × tag on a source object | pid review <project> --approve-rule tagging.isa
vessel.auxiliaries | 80 | 30 × nozzles on a source object, 20 × Component, 20 × ProcessLine, 10 × Instrument | pid review <project> --approve-rule vessel.auxiliaries

## Datasheet data
Open point | Missing data
ur.hw_dn | Hot-water process lines: only a range 'DN 200 à DN 350' is given; per-line diameters are not defined. Branch lines of the cooling-water loop carry only the 'DN 600 minimum' of the main lines.
ur.internal_loop | Internal loop PAC 2A/2B: nominal diameter is 'À définir'; the 50 °C return leg is implied, not stated.
ur.boiler | Gas boiler: capacity, fuel/feed-water/flue connections, PCV technology and failure position are not stated.
ur.tags | Equipment tags are given only for P-030..035, ECH-030..032, TK-001/002, K3/MESSO/GEA and the LPF tanks. Heat pumps, 70/90/RCUA tanks, flash tank, CMV stages, boiler and the new exchangers have no tag.
ur.nozzles | No nozzle numbers or nozzle sizes are given for any equipment (except DN50 on the TGE coil). Nozzle names are schematic.
ur.design_data | No design pressures, relief devices/sizing, safety thresholds (other than 7.5 bar eff.), valve failure positions, material classes or instrument ranges are given. None are invented.
ur.future_hp | PAC 3A/3B are future equipment with no capacity, regime or connection data. They are drawn dashed (LifeCyclePhase=Future) and left unconnected.
ur.gen.fail_position | Failure position (fail open / close / retain) of the control valves is not specified and was not assumed.
ur.gen.instrument_ranges | Measuring ranges and alarm/trip settings of the generated instruments are not specified and were not assumed.
ur.gen.nozzles | Nozzles added for drain, vent and level tapping have no nozzle number and no size.